## Inputs
Pipe Diameter Goal Seek - manual process being replaced
Legend: blue cells are inputs the engineer edits. Black cells are formulas.
Input | Value | Unit | Note |  | SI value
Flow rate Q | 50 | L/s | Design flow | Q (m³/s) | 0.05
Pipe length L | 500 | m | Straight-run length; minor losses not included | L (m) | 500
Absolute roughness ε | 0.045 | mm | Commercial steel (typical handbook value) | ε (m) | 4.5e-05
Kinematic viscosity ν | 1.004 | mm²/s | Water at 20 °C | ν (m²/s) | 1.004e-06
Target head loss h_target | 10 | m | Allowable friction loss
Tolerance | 0.01 | m | Accept when ¦h_f - h_target¦ ≤ tolerance
Gravity g | 9.8066 | m/s² | Standard gravity
Note on B9: Target the engineer tries to hit by changing the trial diameter.

## GoalSeek_Log
Manual goal seek: the engineer types a trial diameter, reads h_f, and adjusts
Laminar (Re < 2000): f = 64/Re. Otherwise Swamee-Jain: f = 0.25 / [log10(ε/(3.7D) + 5.74/Re^0.9)]².
Trial | Diameter D (mm) | Velocity V (m/s) | Reynolds Re | ε/D | Friction f | Head loss h_f (m) | Error ¦h_f - target¦ (m) | Accept?
1 | 100 | 6.3662 | 634083.4386 | 0.00045 | 0.017252 | 178.2449 | 168.2449 | No
2 | 200 | 1.5915 | 317041.7193 | 0.000225 | 0.016412 | 5.2991 | 4.7009 | No
3 | 150 | 2.8294 | 422722.2924 | 0.0003 | 0.016574 | 22.5502 | 12.5502 | No
4 | 175 | 2.0788 | 362333.3935 | 0.00025714 | 0.016454 | 10.3573 | 0.35734 | No
5 | 180 | 1.9649 | 352268.577 | 0.00025 | 0.01644 | 8.9891 | 1.0109 | No
6 | 177 | 2.032 | 358239.2309 | 0.00025424 | 0.016448 | 9.7818 | 0.21819 | No
7 | 176.5 | 2.0436 | 359254.0729 | 0.00025496 | 0.016449 | 9.922 | 0.078002 | No
8 | 176.2 | 2.0505 | 359865.7427 | 0.00025539 | 0.01645 | 10.0073 | 0.0072731 | Yes
Note: each row is one manual guess. There is no iteration limit and no record of why a guess was chosen - the Python tool automates and documents this.